BACnet & Lighting in 2023
Challenges in 1998 when developing a native BACnet networked lighting control system:
Blink Warn
Fade or Step to Level
Group or Zone Actions
Automatic Timeouts (CA - Title 24)
Scenes and Preset Levels
Dawn / Dusk Schedules
The Lighting Applications working group was formed in 2001 to improve BACnet's use as a native network lighting control protocol.
Since then, new BACnet objects, services, properties, and other standard values have been added to the BACnet standard to support lighting control.

---
Object Reliability Property
Object Reliability Property
New standard values were added to Reliability property of objects:
TRIPPED
  - The end device, such as an actuator, is not responding to commands, prevented by a tripped condition or by being mechanically held open.
- LAMP_FAILURE
  - Indicates that the lamp has failed in a physical lighting device.
- COMMUNICATION_FAILURE
  - Proper operation of the object is dependent on communication with a remote sensor or device and communication with the remote sensor or device has been lost.

---
Output Object Interface_Value Property
Output Object Interface_Value Property
HOA (Hand Off Auto) switches are common in control equipment, and permit a local override of output values. Assuming the HOA control cannot be "trumped" by the controller, there is nothing the controller can do to change the value of the output. There is no other process that can change the value of its output. However, the actual output value is of interest (especially to workstations), but are not reportable via a standard mechanism in BACnet, assuming the value of the HOA switch is known by the controller.
Interface_Value
  - This read-only property indicates the value, in engineering units, of the physical output. If the BACnet device is not capable of knowing the value of the physical output, then the value of this property shall be NULL.

---
Lighting Output Object
Lighting Output Object
Present_Value in Percent of Normalized Range
  - 0.0%=Off
  - 1.0-100% =On
  - -1.0 = Warn
  - -2.0 = Warn Relinquish
  - -3.0 = Warn Off
- Lighting_Command for dimming control
  - operation, target level, ramp rate, fade time, step, priority
  - Operations include:
    - fade-to, ramp-to, stop
    - step-up, step-down, step-off
    - warn, warn-relinquish, warn-off
    - restore-on, default-on
    - toggle, toggle-restore, toggle-default
- Internal dimming engine drives Tracking_Value
- Internal Egress_Time timer for automatic relinquish
- Low and High trim to clamp the Present_Value
-4.0 = Restore On
-5.0 = Default On
-6.0 = Toggle Restore
-7.0 = Toggle Default

---
Binary Lighting Output Object
Binary Lighting Output Object
Present_Value is Enumerated for lighting control
  - Off
  - On
  - Warn
  - Warn-relinquish
  - Warn-off
  - Stop
  - + vendor specific if needed
- Internal Egress_Time timer for automatic relinquish
- Strike and Hour counting properties
- Power property
- Optional event notification parameters

---
Channel Object
Channel Object
Writing Device
Present_Value is Channel Value (pseudo Commandable)
  - similar to Any - primitives
  - includes Lighting Command
- Propagated value to List of Object Property References
  - Object Property Reference can be another device
  - Execution Delay + Inhibit
  - Channel Number
  - Group membership
- Defined data coercion
WriteGroup service
WriteProperty service
WritePropertyMultiple service
Device 1
Channel Object
Object
1
Object
2
Object
n
Writing the same value to multiple objects using the Channel object
Device n
Object
1
Object
n

---
WriteGroup Service
WriteGroup Service
- Broadcast Write to Channel Objects in a Single Group
- Group number is designed to limit
  - 0=reserved
  - 1=min
  - 4,294,967,295=max
- Priority - used if not specified
- Change List - Tuples
  - Channel Number = property of Channel object 1-65535
  - Overriding Priority - specific priority if needed
  - Value - may be coerced if not exact datatype
- Inhibit Delay - if allowed by Channel object

---
Staging object
Staging object
The Staging object type provides a way for BACnet devices to map analog values onto multiple Binary
Value, Binary Output, or Binary Lighting Output objects. The Staging object can be used by 0-100% lighting commands that turn on individual fixtures to achieve step-lighting.

---
Timer object
Timer object
Many building automation applications have timer functionality, which should be made network visible for
interoperable control, monitoring, and visualization.
A new object type Timer is added to allow timer functionality to be network visible. A new event algorithm
CHANGE_OF_TIMER is added to accommodate the event detection characteristics and notification needs of the
Timer object.

---
Color object
Color object
The Color object type provides a way for BACnet devices to interact with X,Y color, directly or with control commands:
- None
- Fade To
- Stop
- Override
The Color object is coupled with a Lighting Output object which provides the brightness value.

---
Color Temperature object
Color Temperature object
The Color Temperature object type provides a way for BACnet devices to interact with closest coordinated color temperature (CCT), directly or with control commands:
- None
- Fade To
- Stop
- Override
The Color Temperature object is coupled with a Lighting Output object which provides the brightness value.

---
BACnet - BIBBs - Building Blocks
BACnet - BIBBs - Building Blocks
- Annex K describes the BACnet Interoperability Building Blocks (BIBBs)
- BIBBs used in PICS, standard Profiles
- Example:
  - K.1.2 BIBB
  - Data Sharing-ReadProperty-B (DS-RP-B): The B device is a provider of data to device A.

---
Lighting BIBBs
Lighting BIBBs
With the addition of the Lighting object types and new services, lighting specific BACnet Interoperability Building Blocks (BIBBs) and device profiles were defined.
Lighting Operator Devices and workstations.
This family is composed of B-XAWS, B-ALWS, and B-LOD.
Lighting Control Stations.
This family is composed of B-ALCS and B-LCS.
Lighting Supervisor (button/switch/sensor) and Lighting Device (lamp/ballast).
This family is composed of B-LS and B-LD.

---
BACnet - Key Features
BACnet - Key Features
- Multiple datalink to choose from (Ethernet, WiFi, IPv4, IPv6, IPv6/6LoPAN/802.15.4, EIA-485, etc).
- Optional IT friendly interfaces (RESTful API, JSON responses, object tags) and Security (TLS/websocket)
- Robust objects and services supporting Schedules, Events, Alarms, Audit Logs, Trending, Access Control, Life Safety, Elevators, and Files in addition to many value objects.
- BACnet core interoperability between components is based on an object-oriented model. In this scheme, individual automation system devices can perform any type of function from data sharing to scheduling, from controlling light brightness and color fading to scenes, to integration between HVAC, security, fire and life safety, access control.
- Each device, whether it is a controller or an endpoint, can participate in the BACnet network, and has its own identity.

---
BACnet Objects for Modeling a Device
BACnet Objects for Modeling a Device
accumulator
binary-output
file
multi-state-output
trend-log
analog-input
binary-value
group
multi-state-value
load-control
structured-view
analog-output
calendar
life-safety-point
notification-class
analog-value
command
life-safety-zone
program
trend-log-multiple
averaging
device
loop
pulse-converter
binary-input
credential-data-input
event-enrollment
multi-state-input
schedule
event-log
access-credential
access-zone
access-rights
access-point
access-user
access-door
bitstring-value
global-group
characterstring-value
characterstring-value
date-value
datetime-pattern-value
datetime-value
integer-value
date-pattern-value
octetstring-value
positive-integer-value
time-pattern-value
time-value
large-analog-value
channel
network-security
timer
lighting-output
binary-lighting-output
notification-forwarder
alert-enrollment
network-port
elevator-group
escalator
lift
staging
audit-log
audit-reporter
color
color-temperature

---
BACnet Object Property Values
BACnet Object Property Values
For 'value' objects, additional property values assist the building or application integration to understand other related information of the 'value', such as Units, Status or Name and provide a vendor a rich palette from which to model their device features.

---
BACnet Confirmed Services
BACnet Confirmed Services
Confirmed == Unicast, Acknowledged
AtomicWriteFile
WritePropertyMultiple
AcknowledgeAlarm
PrivateTransfer
COV-Notification
AddListElement
RemoveListElement
TextMessage
EventNotification
GetAlarmSummary
CreateObject
ReinitializeDevice
DeleteObject
VTOpen
GetEnrollmentSummary
SubscribeCOV
ReadProperty
VTClose
VTData
SubscribeCOVProperty
ReadPropertyMultiple
Authenticate
LifeSafetyOperation
ReadRange
RequestKey
AtomicReadFile
WriteProperty
AuditLogQuery
GetEventInformation
ReadPropertyConditional
ConfirmedCOVNotificationMultiple
DeviceCommunicationControl
SubscribeCOVPropertyMultiple

---
BACnet Confirmed Services
BACnet Confirmed Services
Unconfirmed == Broadcast (usually)
I-Am
TextMessage
I-Have
TimeSynchronization
COV-Notification
WhoHas
EventNotification
WhoIs
PrivateTransfer
UTC-TimeSynchronization
WriteGroup
COV-NotificationMultiple
Who-Am-I
AuditNotification
You-Are

---
BACnet Application Layer
Design: BACnet object modeling for Lighting Control
Required
Device object
Network Port object
Lighting Specific Outputs
Lighting Output object
Binary Lighting Output object
Staging object
Color object
Color Temperature object
Shades & Blinds
Analog Output object
Binary Output object
Multi-state Output object
Sensors (light, motion, touch)
Analog Input object
Binary Input object
Multi-state Input object
Demand Response/Shed
Load Control object
Averaging object
Grouping Lights
Channel object
Daylight Harvesting
Loop object
Area Timeout
Timer object
Time of Day Scheduling
Schedule object
Calendar object
Configuration Parameters
Analog Value object
Binary Value object
Multi-state Value object

---
BACnet Application Layer
Design: BACnet Network Communication
BACnet Application Layer
Design: BACnet Network Communication
Object property services
ReadProperty
WriteProperty
ReadPropertyMultiple
WritePropertyMultiple
Control services
WriteGroup
WriteProperty
Device discovery and management services
ReinitializeDevice
DeviceCommunicationControl
Who-Am-I
You-Are
Who-Is
I-Am
Other object services
AtomicReadFile
AtomicWriteFile
COVNotification
SubscribeCOV
Other Device services
TimeSynchronization
UTCTimeSynchronization
Peer to Peer control is possible with any device!
Native BACnet vs Gateway
Gateway adds latency
Gateway restricts the BACnet service & object property model
Gateway requires a translation from the downstream protocol

---
BACnet Application Layer
Design: Extensibility
BACnet Application Layer
Design: Extensibility
Vendors can create their own services using Confirmed or Unconfirmed Private Transfer for services that BACnet hasn't standardized:
Tunnel non-BACnet protocols
Send Non-BACnet notifications or events
Enable vendor specific features
Vendors can create their own objects with their own set of properties for objects that BACnet hasn't standardized:
Only required to have object name, type, and instance properties
Vendors can add their own properties to BACnet standard objects
Many of the enumerations used in standard BACnet object property value and services are vendor extensible
BACnet Vendor ID is free to any entity

---
BACnet - Color & Lights & Sensors
BACnet - Color & Lights & Sensors
Power Over Ethernet
Sensing devices use BACnet services to directly control other BACnet device objects, or to notify other BACnet building controllers
IEEE 802.3af-2003 PoE 15.4 W
IEEE 802.3at-2009 PoE+ 25.5 W
IEEE 802.3bt-2018 PoE++ 51 W
IEEE 802.3bt-2018 4PPoE 71.3 W
IEEE 802.3bu-2016 PoDL 50 W
There are IP migration transmission systems called ‘IP over any cable’ technology on the market today that allow installers/end-users to take advantage of extended PoE power & Ethernet distances using legacy cable.

---
BACnet Integration - Vivarium
BACnet Integration - Vivarium
Environmental controls
- Lighting - A lighting system simulates the requirements of the animal and plant species, such as day/night regulator
- Temperature - simulates conditions found in their natural habitat, including simulated day/night or seasonal periods
- Humidity - simulates conditions found in their natural habitat, including simulated day/night or seasonal periods
- Ventilation and openings - Access inside the vivarium is required for the purpose of maintenance, sometimes with the use of special lighting that won't disrupt experiments or the species inside

---
BACnet - Key Benefits
BACnet - Key Benefits
- Worldwide standardized data communication for building automation
- Independent of specific technologies and suppliers
- Comprehensive solution for building control and automation networks
- Compatibility with IT infrastructure and highly scalable solutions
- Validation at independent testing laboratories and product certification
- Continuously being maintained and upgraded while preserving current investments